## Assumptions
Floating Offshore Wind Farm — Cost Model
Dynamic line-item cost breakdown, rolling up to full wind-farm level. Real 2024 prices (£).
Site definition
Wind farm rating | 1000 | MW | Total installed capacity — drives every full-farm total
Turbine rating | 15 | MW
Number of turbines
Water depth at site | 100 | m
Annual mean wind speed at 100 m | 10 | m/s
Offshore substation to shore | 75 | km
Shore to onshore substation | 10 | km
Programme
Year of FID | 2028 |  | Discounting base year (t = 0)
First operation date | 2030
Construction period | 2 | years | CAPEX spread across the years before first operation
Operational life | 30 | years | Assumption — used for OPEX lifetime and LCOE
Financial & energy
Discount rate (WACC) | 8% |  | Real, pre-tax; used for LCOE discounting
Gross capacity factor | 55% |  | Before availability & electrical losses
Availability | 95% |  | Technical availability of the wind farm
Electrical / transmission losses | 3% |  | Array + export + substation losses
Net load factor
Net annual energy (AEP) |  | MWh/yr
Cells shaded orange are inputs — change them and the whole model recalculates. All other figures are formulas.

## Cost Breakdown
Cost Breakdown Structure
Line items roll up to assemblies and full wind-farm level. Use the +/− outline buttons on the left to collapse each assembly.
Cost item | Unit | Rate | Wind farm total | Stated (source) | Variance
CAPEX — Capital expenditure (one-off) | £/MW
Development and project management | £/MW |  |  | 155000
Development and consenting services | £/MW |  |  | 72000
Environmental impact assessments | £/MW | 11000 |  | 11000
Development activities and other consenting services | £/MW | 62000 |  | 62000
Environmental surveys | £/MW |  |  | 9000
Animal surveys (benthic, fish, shellfish, mammals and birds) | £/MW | 7000 |  | 7000
Onshore environmental surveys | £/MW | 1000 |  | 1000
Human impact studies | £/MW | 1000 |  | 1000
Resource and metocean assessment | £/MW |  |  | 7000
Structure | £/MW | 4000 |  | 4000
Sensors | £/MW | 3000 |  | 3000
Maintenance | £/MW | 1000 |  | 1000
Geological and hydrographical surveys | £/MW |  |  | 9000
Geophysical surveys | £/MW | 3000 |  | 3000
Geotechnical surveys | £/MW | 5000 |  | 5000
Hydrographic surveys | £/MW | 2000 |  | 2000
Engineering and consultancy | £/MW | 9000 |  | 9000
Project management | £/MW | 48000 |  | 48000
Wind turbine | £/MW |  |  | 1350000
Nacelle | £/MW | 834000 |  | 834000
Rotor | £/MW | 360000 |  | 360000
Tower | £/MW | 156000 |  | 156000
Balance of plant | £/MW |  |  | 2418000
Dynamic array cable | £/MW | 115000 |  | 115000
Export cable | £/MW | 269000 |  | 269000
Cable accessories | £/MW |  |  | 80000
Interface | £/MW | 30000 |  | 30000
Cable protection | £/MW | 4000 |  | 4000
Buoyancy | £/MW | 2000 |  | 2000
Connectors and joints | £/MW | 43000 |  | 43000
Floating substructure | £/MW |  |  | 1313000
Structure | £/MW | 1103000 |  | 1103000
Secondary steel | £/MW | 53000 |  | 53000
Systems | £/MW | 92000 |  | 92000
Corrosion protection | £/MW | 65000 |  | 65000
Mooring systems | £/MW |  |  | 316000
Anchor systems | £/MW | 35000 |  | 35000
Mooring lines and chains | £/MW | 174000 |  | 174000
Jewellery | £/MW | 98000 |  | 98000
Topside connection | £/MW | 6000 |  | 6000
Installation aids | £/MW | 3000 |  | 3000
Offshore substation | £/MW |  |  | 282000
HVAC electrical system | £/MW | 80000 |  | 80000
Auxiliary systems | £/MW | 13000 |  | 13000
Topside structure | £/MW | 123000 |  | 123000
Foundation | £/MW | 65000 |  | 65000
Onshore substation | £/MW |  |  | 44000
Electrical system | £/MW | 31000 |  | 31000
Buildings, access and security | £/MW | 13000 |  | 13000
Installation and commissioning | £/MW |  |  | 1376000
Inbound transport | £/MW | 154000 |  | 154000
Mooring and anchoring pre-installation | £/MW | 153000 |  | 153000
Floating substructure - turbine assembly | £/MW |  |  | 72000
Crane and lifting equipment | £/MW | 34000 |  | 34000
Technician services | £/MW | 11000 |  | 11000
Marshalling port | £/MW | 22000 |  | 22000
Other | £/MW | 5000 |  | 5000
Floating substructure - turbine installation | £/MW | 114000 |  | 114000
Offshore cable installation | £/MW | 171000 |  | 171000
Onshore export cable installation | £/MW | 8000 |  | 8000
Offshore substation installation | £/MW | 52000 |  | 52000
Onshore substation construction | £/MW | 29000 |  | 29000
Offshore logistics | £/MW |  |  | 13000
Sea-based support | £/MW | 6000 |  | 6000
Marine coordination | £/MW | 2000 |  | 2000
Weather forecasting and metocean data | £/MW | 1000 |  | 1000
Marine safety and rescue | £/MW | 4000 |  | 4000
Contingency and insurance | £/MW | 610000 |  | 610000
TOTAL CAPEX (build cost)
OPEX — Operating expenditure (annual) | £/MW/yr
Operation, maintenance and service | £/MW/yr |  |  | 98000
Operations, maintenance and service port | £/MW/yr | 0 |  | 0
Operations | £/MW/yr |  |  | 34000
Operations control centre | £/MW/yr | 1000 |  | 1000
Training | £/MW/yr | 3000 |  | 3000
Onshore logistics | £/MW/yr | 1000 |  | 1000
Technical resource (onshore and off) | £/MW/yr | 7000 |  | 7000
Admin and support staff (onshore) | £/MW/yr | 8000 |  | 8000
Insurance | £/MW/yr | 14000 |  | 14000
Offshore logistics | £/MW/yr | 7000 |  | 7000
Maintenance and service | £/MW/yr |  |  | 57000
Turbine maintenance and service | £/MW/yr | 41000 |  | 41000
Balance of plant maintenance and service | £/MW/yr | 15000 |  | 15000
Statutory inspections | £/MW/yr | 1000 |  | 1000
TOTAL OPEX (per year)
DECEX — Decommissioning (end of life) | £/MW
Decommissioning | £/MW |  |  | 450000
Floating hull - turbine decommissioning | £/MW | 148000 |  | 148000
Mooring and anchoring decommissioning | £/MW | 122000 |  | 122000
Cable decommissioning | £/MW | 137000 |  | 137000
Substation decommissioning | £/MW | 42000 |  | 42000
TOTAL DECEX (decommissioning)
LIFETIME COST (CAPEX + OPEX×life + DECEX) | £/MW
Notes: 'Rate' leaf cells are inputs; every assembly/category is =SUM(children), so editing a line item rolls up automatically. 'Wind farm total' = Rate × farm rating (£/yr for OPEX rows). 'Stated (source)' is the published rounded figure; 'Variance' is the small rounding gap between the computed roll-up and the published total.

## Lifetime Summary
Lifetime Cost Summary
Contribution of each major cost element to whole-life cost of the wind farm.
Cost element | Lifetime cost (£) | Per MW (£/MW) | % of total
Development and project management
Wind turbine
Balance of plant
Installation and commissioning
Operation, maintenance and service
Decommissioning
TOTAL LIFETIME COST

## LCOE
Levelised Cost of Energy (LCOE)
Discounted cash-flow model. LCOE = Σ(discounted cost) / Σ(discounted energy), discounted to the year of FID.
LCOE
£ per MWh, real 2024, discounted to FID
Year | t | CAPEX (£) | OPEX (£) | DECEX (£) | Total cost (£) | Energy (MWh) | Discount factor | Disc. cost (£) | Disc. energy (MWh)
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
Totals